{"text_format":"5","workbook":"xlsx","n_sheets":1,"sheets":["Measurement Busbar 10 kV"],"props":{"creator":"Jonas Schäfer","last_modified_by":"Jonas Schäfer","company":"DigSILENT GmbH"},"read":"whole","date_system":"1900"}

{"sheet":"Measurement Busbar 10 kV","index":0,"n_rows":41,"n_cols":13,"rows_kept":41}
["Frequency","Voltage Phase A, % of Unom,","Voltage Phase B, % of Unom,","Voltage Phase C, % of Unom,","Angle Ua","Angle Ub","Angle Uc","U1 in % of Unom","U2 in % of Unom","U0 in % of Unom","Angle U1","Angle U2","Angle U0"]
[50,{"v":100,"d":"100.00"},{"v":100,"d":"100.00"},{"v":100,"d":"100.00"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"$f":"SQRT((B2*COS(E2*PI()/180)+C2*COS((F2+120)*PI()/180)+D2*COS((G2-120)*PI()/180))^2+(B2*SIN(E2*PI()/180)+C2*SIN((F2+120)*PI()/180)+D2*SIN((G2-120)*PI()/180))^2)/3","v":{"v":100,"d":"100.00"}},{"$f":"SQRT((B2*COS(E2*PI()/180)+C2*COS((F2-120)*PI()/180)+D2*COS((G2+120)*PI()/180))^2+(B2*SIN(E2*PI()/180)+C2*SIN((F2-120)*PI()/180)+D2*SIN((G2+120)*PI()/180))^2)/3","v":{"v":2.842170943040401e-14,"d":"0.00"}},{"$f":"SQRT((B2*COS(E2*PI()/180)+C2*COS((F2)*PI()/180)+D2*COS((G2)*PI()/180))^2+(B2*SIN(E2*PI()/180)+C2*SIN((F2)*PI()/180)+D2*SIN((G2)*PI()/180))^2)/3","v":{"v":1.4210854715202004E-14,"d":"0.00"}},{"$f":"ATAN2((B2*COS(E2*PI()/180)+C2*COS((F2+120)*PI()/180)+D2*COS((G2-120)*PI()/180)),(B2*SIN(E2*PI()/180)+C2*SIN((F2+120)*PI()/180)+D2*SIN((G2-120)*PI()/180)))*180/PI()","v":{"v":0,"d":"0.00"}},{"$f":"ATAN2((B2*COS(E2*PI()/180)+C2*COS((F2-120)*PI()/180)+D2*COS((G2+120)*PI()/180)),(B2*SIN(E2*PI()/180)+C2*SIN((F2-120)*PI()/180)+D2*SIN((G2+120)*PI()/180)))*180/PI()","v":{"v":180,"d":"180.00"}},{"$f":"ATAN2((B2*COS(E2*PI()/180)+C2*COS((F2)*PI()/180)+D2*COS((G2)*PI()/180)),(B2*SIN(E2*PI()/180)+C2*SIN((F2)*PI()/180)+D2*SIN((G2)*PI()/180)))*180/PI()","v":{"v":0,"d":"0.00"}}]
[100,{"v":0.1,"d":"0.10"},{"v":0.3,"d":"0.30"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"$f":"SQRT((B3*COS(E3*PI()/180)+C3*COS((F3+120)*PI()/180)+D3*COS((G3-120)*PI()/180))^2+(B3*SIN(E3*PI()/180)+C3*SIN((F3+120)*PI()/180)+D3*SIN((G3-120)*PI()/180))^2)/3","v":{"v":0.08819171036881979,"d":"0.09"}},{"$f":"SQRT((B3*COS(E3*PI()/180)+C3*COS((F3-120)*PI()/180)+D3*COS((G3+120)*PI()/180))^2+(B3*SIN(E3*PI()/180)+C3*SIN((F3-120)*PI()/180)+D3*SIN((G3+120)*PI()/180))^2)/3","v":{"v":0.26666666666666666,"d":"0.27"}},{"$f":"SQRT((B3*COS(E3*PI()/180)+C3*COS((F3)*PI()/180)+D3*COS((G3)*PI()/180))^2+(B3*SIN(E3*PI()/180)+C3*SIN((F3)*PI()/180)+D3*SIN((G3)*PI()/180))^2)/3","v":{"v":0.08819171036881963,"d":"0.09"}},{"$f":"ATAN2((B3*COS(E3*PI()/180)+C3*COS((F3+120)*PI()/180)+D3*COS((G3-120)*PI()/180)),(B3*SIN(E3*PI()/180)+C3*SIN((F3+120)*PI()/180)+D3*SIN((G3-120)*PI()/180)))*180/PI()","v":{"v":160.89339464913093,"d":"160.89"}},{"$f":"ATAN2((B3*COS(E3*PI()/180)+C3*COS((F3-120)*PI()/180)+D3*COS((G3+120)*PI()/180)),(B3*SIN(E3*PI()/180)+C3*SIN((F3-120)*PI()/180)+D3*SIN((G3+120)*PI()/180)))*180/PI()","v":{"v":0,"d":"0.00"}},{"$f":"ATAN2((B3*COS(E3*PI()/180)+C3*COS((F3)*PI()/180)+D3*COS((G3)*PI()/180)),(B3*SIN(E3*PI()/180)+C3*SIN((F3)*PI()/180)+D3*SIN((G3)*PI()/180)))*180/PI()","v":{"v":-160.89339464913087,"d":"-160.89"}}]
[150,{"v":0.4,"d":"0.40"},{"v":0.5,"d":"0.50"},{"v":0.1,"d":"0.10"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.12018504251546631,"d":"0.12"},{"v":0.12018504251546631,"d":"0.12"},{"v":0.3333333333333333,"d":"0.33"},{"v":73.89788624801396,"d":"73.90"},{"v":-73.89788624801396,"d":"-73.90"},{"v":0,"d":"0.00"}]
[200,{"v":1,"d":"1.00"},{"v":1.3,"d":"1.30"},{"v":0.6,"d":"0.60"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.9666666666666667,"d":"0.97"},{"v":0.20275875100994056,"d":"0.20"},{"v":0.20275875100994067,"d":"0.20"},{"v":0,"d":"0.00"},{"v":85.28499604605186,"d":"85.28"},{"v":-85.28499604605175,"d":"-85.28"}]
[250,{"v":2,"d":"2.00"},{"v":3,"d":"3.00"},{"v":1.5,"d":"1.50"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.44095855184409843,"d":"0.44"},{"v":2.1666666666666665,"d":"2.17"},{"v":0.4409585518440984,"d":"0.44"},{"v":-100.893394649131,"d":"-100.89"},{"v":0,"d":"0.00"},{"v":100.89339464913087,"d":"100.89"}]
[300,{"v":0.9,"d":"0.90"},{"v":0.8,"d":"0.80"},{"v":0.9,"d":"0.90"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.033333333333333395,"d":"0.03"},{"v":0.033333333333333395,"d":"0.03"},{"v":0.8666666666666667,"d":"0.87"},{"v":-59.99999999999978,"d":"-60.00"},{"v":59.99999999999978,"d":"60.00"},{"v":0,"d":"0.00"}]
[350,{"v":1.1,"d":"1.10"},{"v":1.4,"d":"1.40"},{"v":0.9,"d":"0.90"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":1.1333333333333333,"d":"1.13"},{"v":0.14529663145135577,"d":"0.15"},{"v":0.14529663145135574,"d":"0.15"},{"v":0,"d":"0.00"},{"v":96.5867755536296,"d":"96.59"},{"v":-96.58677555362937,"d":"-96.59"}]
[400,{"v":0.3,"d":"0.30"},{"v":0.5,"d":"0.50"},{"v":0.6,"d":"0.60"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.08819171036881984,"d":"0.09"},{"v":0.4666666666666666,"d":"0.47"},{"v":0.08819171036881962,"d":"0.09"},{"v":160.89339464913093,"d":"160.89"},{"v":0,"d":"0.00"},{"v":-160.89339464913087,"d":"-160.89"}]
[450,{"v":0.2,"d":"0.20"},{"v":0.1,"d":"0.10"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.057735026918962574,"d":"0.06"},{"v":0.057735026918962574,"d":"0.06"},{"v":0.20000000000000004,"d":"0.20"},{"v":-89.99999999999997,"d":"-90.00"},{"v":89.99999999999997,"d":"90.00"},{"v":0,"d":"0.00"}]
[500,{"v":0.4,"d":"0.40"},{"v":0.3,"d":"0.30"},{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.39999999999999997,"d":"0.40"},{"v":0.05773502691896256,"d":"0.06"},{"v":0.057735026918962574,"d":"0.06"},{"v":0,"d":"0.00"},{"v":-90.0000000000001,"d":"-90.00"},{"v":89.99999999999993,"d":"90.00"}]
[550,{"v":0.7,"d":"0.70"},{"v":0.6,"d":"0.60"},{"v":0.9,"d":"0.90"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.08819171036881972,"d":"0.09"},{"v":0.7333333333333333,"d":"0.73"},{"v":0.08819171036881968,"d":"0.09"},{"v":100.89339464913105,"d":"100.89"},{"v":0,"d":"0.00"},{"v":-100.89339464913083,"d":"-100.89"}]
[600,{"v":0.2,"d":"0.20"},{"v":0.2,"d":"0.20"},{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":2.7755575615628914E-17,"d":"0.00"},{"v":2.7755575615628914E-17,"d":"0.00"},{"v":0.20000000000000004,"d":"0.20"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[650,{"v":0.2,"d":"0.20"},{"v":0.1,"d":"0.10"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.23333333333333336,"d":"0.23"},{"v":0.08819171036881968,"d":"0.09"},{"v":0.08819171036881969,"d":"0.09"},{"v":0,"d":"0.00"},{"v":-100.89339464913095,"d":"-100.89"},{"v":100.89339464913087,"d":"100.89"}]
[700,{"v":0.4,"d":"0.40"},{"v":0.4,"d":"0.40"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.03333333333333328,"d":"0.03"},{"v":0.3666666666666667,"d":"0.37"},{"v":0.03333333333333337,"d":"0.03"},{"v":-60.00000000000014,"d":"-60.00"},{"v":0,"d":"0.00"},{"v":59.99999999999993,"d":"60.00"}]
[750,{"v":0.2,"d":"0.20"},{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.0666666666666667,"d":"0.07"},{"v":0.0666666666666667,"d":"0.07"},{"v":0.13333333333333333,"d":"0.13"},{"v":59.99999999999999,"d":"60.00"},{"v":-59.99999999999999,"d":"-60.00"},{"v":0,"d":"0.00"}]
[800,{"v":0.1,"d":"0.10"},{"v":0.2,"d":"0.20"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.23333333333333336,"d":"0.23"},{"v":0.08819171036881975,"d":"0.09"},{"v":0.08819171036881966,"d":"0.09"},{"v":0,"d":"0.00"},{"v":-139.10660535086913,"d":"-139.11"},{"v":139.10660535086905,"d":"139.11"}]
[850,{"v":0.4,"d":"0.40"},{"v":0.5,"d":"0.50"},{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.03333333333333347,"d":"0.03"},{"v":0.4666666666666666,"d":"0.47"},{"v":0.03333333333333325,"d":"0.03"},{"v":180,"d":"180.00"},{"v":0,"d":"0.00"},{"v":180,"d":"180.00"}]
[900,{"v":0.5,"d":"0.50"},{"v":0.1,"d":"0.10"},{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.12018504251546631,"d":"0.12"},{"v":0.12018504251546631,"d":"0.12"},{"v":0.26666666666666666,"d":"0.27"},{"v":-13.897886248013988,"d":"-13.90"},{"v":13.897886248013988,"d":"13.90"},{"v":0,"d":"0.00"}]
[950,{"v":0.1,"d":"0.10"},{"v":0.5,"d":"0.50"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.3333333333333333,"d":"0.33"},{"v":0.12018504251546645,"d":"0.12"},{"v":0.12018504251546624,"d":"0.12"},{"v":0,"d":"0.00"},{"v":166.10211375198605,"d":"166.10"},{"v":-166.10211375198602,"d":"-166.10"}]
[1000,{"v":0.1,"d":"0.10"},{"v":0.3,"d":"0.30"},{"v":0.1,"d":"0.10"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.06666666666666668,"d":"0.07"},{"v":0.16666666666666666,"d":"0.17"},{"v":0.06666666666666665,"d":"0.07"},{"v":-120.00000000000004,"d":"-120.00"},{"v":0,"d":"0.00"},{"v":119.99999999999997,"d":"120.00"}]
[1050,{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.1666666666666667,"d":"0.17"},{"v":0.1666666666666667,"d":"0.17"},{"v":0.3333333333333333,"d":"0.33"},{"v":-59.99999999999999,"d":"-60.00"},{"v":59.99999999999999,"d":"60.00"},{"v":0,"d":"0.00"}]
[1100,{"v":0,"d":"0.00"},{"v":0.5,"d":"0.50"},{"v":0.1,"d":"0.10"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.19999999999999998,"d":"0.20"},{"v":0.1527525231651947,"d":"0.15"},{"v":0.15275252316519464,"d":"0.15"},{"v":0,"d":"0.00"},{"v":130.89339464913095,"d":"130.89"},{"v":-130.8933946491309,"d":"-130.89"}]
[1150,{"v":0.3,"d":"0.30"},{"v":0.2,"d":"0.20"},{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.03333333333333327,"d":"0.03"},{"v":0.2333333333333333,"d":"0.23"},{"v":0.03333333333333335,"d":"0.03"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[1200,{"v":0.2,"d":"0.20"},{"v":0.4,"d":"0.40"},{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.06666666666666665,"d":"0.07"},{"v":0.06666666666666665,"d":"0.07"},{"v":0.26666666666666666,"d":"0.27"},{"v":119.99999999999997,"d":"120.00"},{"v":-119.99999999999997,"d":"-120.00"},{"v":0,"d":"0.00"}]
[1250,{"v":0.1,"d":"0.10"},{"v":0,"d":"0.00"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.16666666666666666,"d":"0.17"},{"v":0.12018504251546629,"d":"0.12"},{"v":0.12018504251546631,"d":"0.12"},{"v":0,"d":"0.00"},{"v":-106.10211375198604,"d":"-106.10"},{"v":106.102113751986,"d":"106.10"}]
[1300,{"v":0.2,"d":"0.20"},{"v":0.2,"d":"0.20"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.03333333333333336,"d":"0.03"},{"v":0.2333333333333333,"d":"0.23"},{"v":0.03333333333333331,"d":"0.03"},{"v":120.00000000000011,"d":"120.00"},{"v":0,"d":"0.00"},{"v":-119.99999999999994,"d":"-120.00"}]
[1350,{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.06666666666666667,"d":"0.07"},{"v":0.06666666666666667,"d":"0.07"},{"v":0.06666666666666667,"d":"0.07"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[1400,{"v":0.4,"d":"0.40"},{"v":0.3,"d":"0.30"},{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.39999999999999997,"d":"0.40"},{"v":0.05773502691896256,"d":"0.06"},{"v":0.057735026918962574,"d":"0.06"},{"v":0,"d":"0.00"},{"v":-90.0000000000001,"d":"-90.00"},{"v":89.99999999999993,"d":"90.00"}]
[1450,{"v":0.2,"d":"0.20"},{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.14529663145135577,"d":"0.15"},{"v":0.2333333333333333,"d":"0.23"},{"v":0.14529663145135577,"d":"0.15"},{"v":-96.5867755536295,"d":"-96.59"},{"v":0,"d":"0.00"},{"v":96.58677555362944,"d":"96.59"}]
[1500,{"v":0.5,"d":"0.50"},{"v":0.3,"d":"0.30"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.05773502691896263,"d":"0.06"},{"v":0.05773502691896263,"d":"0.06"},{"v":0.4000000000000001,"d":"0.40"},{"v":-29.99999999999998,"d":"-30.00"},{"v":29.99999999999998,"d":"30.00"},{"v":0,"d":"0.00"}]
[1550,{"v":0.5,"d":"0.50"},{"v":0.5,"d":"0.50"},{"v":0.1,"d":"0.10"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.3666666666666667,"d":"0.37"},{"v":0.13333333333333325,"d":"0.13"},{"v":0.13333333333333333,"d":"0.13"},{"v":0,"d":"0.00"},{"v":60.00000000000002,"d":"60.00"},{"v":-59.999999999999986,"d":"-60.00"}]
[1600,{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.12018504251546626,"d":"0.12"},{"v":0.2333333333333333,"d":"0.23"},{"v":0.12018504251546634,"d":"0.12"},{"v":46.102113751986025,"d":"46.10"},{"v":0,"d":"0.00"},{"v":-46.10211375198601,"d":"-46.10"}]
[1650,{"v":0.3,"d":"0.30"},{"v":0.2,"d":"0.20"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.05773502691896259,"d":"0.06"},{"v":0.05773502691896259,"d":"0.06"},{"v":0.3,"d":"0.30"},{"v":-89.99999999999997,"d":"-90.00"},{"v":89.99999999999997,"d":"90.00"},{"v":0,"d":"0.00"}]
[1700,{"v":0.3,"d":"0.30"},{"v":0.1,"d":"0.10"},{"v":0.1,"d":"0.10"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.16666666666666666,"d":"0.17"},{"v":0.06666666666666664,"d":"0.07"},{"v":0.06666666666666667,"d":"0.07"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"}]
[1750,{"v":0.2,"d":"0.20"},{"v":0.5,"d":"0.50"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.0881917103688198,"d":"0.09"},{"v":0.3666666666666667,"d":"0.37"},{"v":0.08819171036881962,"d":"0.09"},{"v":-160.89339464913093,"d":"-160.89"},{"v":0,"d":"0.00"},{"v":160.89339464913093,"d":"160.89"}]
[1800,{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":0.5,"d":"0.50"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.1452966314513558,"d":"0.15"},{"v":0.1452966314513558,"d":"0.15"},{"v":0.26666666666666666,"d":"0.27"},{"v":-83.41322444637052,"d":"-83.41"},{"v":83.41322444637052,"d":"83.41"},{"v":0,"d":"0.00"}]
[1850,{"v":0,"d":"0.00"},{"v":0.4,"d":"0.40"},{"v":0.2,"d":"0.20"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.20000000000000004,"d":"0.20"},{"v":0.11547005383792523,"d":"0.12"},{"v":0.11547005383792512,"d":"0.12"},{"v":0,"d":"0.00"},{"v":150.00000000000003,"d":"150.00"},{"v":-149.99999999999997,"d":"-150.00"}]
[1900,{"v":0.3,"d":"0.30"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":120,"d":"120.00"},{"v":-120,"d":"-120.00"},{"v":0.09999999999999996,"d":"0.10"},{"v":0.19999999999999998,"d":"0.20"},{"v":0.10000000000000002,"d":"0.10"},{"v":-60.00000000000002,"d":"-60.00"},{"v":0,"d":"0.00"},{"v":59.99999999999999,"d":"60.00"}]
[1950,{"v":0,"d":"0.00"},{"v":0.2,"d":"0.20"},{"v":0.4,"d":"0.40"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0,"d":"0.00"},{"v":0.11547005383792512,"d":"0.12"},{"v":0.11547005383792512,"d":"0.12"},{"v":0.20000000000000004,"d":"0.20"},{"v":-149.99999999999997,"d":"-150.00"},{"v":149.99999999999997,"d":"150.00"},{"v":0,"d":"0.00"}]
[2000,{"v":0.5,"d":"0.50"},{"v":0.5,"d":"0.50"},{"v":0.3,"d":"0.30"},{"v":0,"d":"0.00"},{"v":-120,"d":"-120.00"},{"v":120,"d":"120.00"},{"v":0.43333333333333335,"d":"0.43"},{"v":0.0666666666666666,"d":"0.07"},{"v":0.0666666666666667,"d":"0.07"},{"v":0,"d":"0.00"},{"v":60.000000000000085,"d":"60.00"},{"v":-59.99999999999996,"d":"-60.00"}]